## Slide 1
Unidad Concentradora
Unidad de Medida
Visualizador
Acceso Local
ePlusMobile
I0
I3
I4
Backend
Integration
Cloud Queue
Cloud
File Storage
CSV
I6
SMMePlus integration platform
Reports
SMMePlus
DB
DB Read only
Distributor Company Stakeholder
I7
I8
DB Enel distributor legacy system
I8
Old Version
I0
Notes: The I0 interface allows local communication with the Measurement Unit and, if it exists, with the Concentrator Unit. The permissions may only be read, or read and write, depending on the authorization of the authorized personnel.
The I1 interface enables the display of data from the Unit of Measure to the Visualizer, when applicable, and with read-only permission.
Interfaces I2, I3 and I4 allow communication between the Measurement Unit and the Management and Operation System, between the Measurement Unit and the Concentrator Unit and between the Concentrator Unit and the Management and Operation System, respectively.
All of them with read and write permissions in both directions, as appropriate.
The I5 interface allows the Distribution Company to save the required information in the Central Database, and to access it in order to guarantee its integrity.
The I6 interface allows communication between the Management and Operation System with other systems and applications of the Distribution Company, with read and write permission in both directions, as appropriate.
The I7 interface allows communication between the Central Database and the Data and Report Warehouse, and with read-only permission.
The I8 interface allows authorized Stakeholders access to information from the Central Database. They will have read-only permissions, and the collection of information may be automatic, scheduled and periodic, or upon request, as defined.
The I9 and I10 interfaces will act as I7 and I8 interfaces, respectively, in case the Data Operator is created.
The I11 and I12 interfaces enable communication between the value added electrical services and the SMMC and the systems and applications of the Distribution Company, respectively. Permissions may be read only, or read and deed, as appropriate, and must be authorized by the Superintendency. In any case, the Client and / or User must authorize the use of their data as established in Chapter 8 of this Technical Annex.

## Slide 2
Unidad Concentradora
Unidad de Medida
Visualizador
Acceso Local
ePlusMobile
I0
I3
I4
Backend
Integration
Services
Cloud Queue
Cloud
File Storage
CSV
I6
integration Platform
Reports
AMI - HES
DB
DB Read only
Distributor Company Stakeholders
I5
I8
DB Enel distributor legacy system
I8
I7
usuario
Actualización PFC
I0
Notes: The I0 interface allows local communication with the Measurement Unit and, if it exists, with the Concentrator Unit. The permissions may only be read, or read and write, depending on the authorization of the authorized personnel.
The I1 interface enables the display of data from the Unit of Measure to the Visualizer, when applicable, and with read-only permission.
Interfaces I2, I3 and I4 allow communication between the Measurement Unit and the Management and Operation System, between the Measurement Unit and the Concentrator Unit and between the Concentrator Unit and the Management and Operation System, respectively.
All of them with read and write permissions in both directions, as appropriate.
The I5 interface allows the Distribution Company to save the required information in the Central Database, and to access it in order to guarantee its integrity.
The I6 interface allows communication between the Management and Operation System with other systems and applications of the Distribution Company, with read and write permission in both directions, as appropriate.
The I7 interface allows communication between the Central Database and the Data and Report Warehouse, and with read-only permission.
The I8 interface allows authorized Stakeholders access to information from the Central Database. They will have read-only permissions, and the collection of information may be automatic, scheduled and periodic, or upon request, as defined.
The I9 and I10 interfaces will act as I7 and I8 interfaces, respectively, in case the Data Operator is created.
The I11 and I12 interfaces enable communication between the value added electrical services and the SMMC and the systems and applications of the Distribution Company, respectively. Permissions may be read only, or read and deed, as appropriate, and must be authorized by the Superintendency. In any case, the Client and / or User must authorize the use of their data as established in Chapter 8 of this Technical Annex.

## Slide 3
Unidad Concentradora
Unidad de Medida
Visualizador
Windows Time
usuario
Server
AMI - HES
DB
DB Read only
Sync Own Activity
Sync
Own Activity
Sync meter Activity
I3
I4
I5
Actualización PFC

## Slide 4
Almacén y Reportes
Partes interesadas
Base de Datos
SGO
AMI - HES
DB
I7
I8
Actualización PFC

## Slide 5
I6
I6
Cloud Queue
ePlus
ePlus
Integration Services
Enel Distibutor Legacy Systems
Legacy Integration
Database
ePlus
System
SMMePlus Integration Platform
IntegradorEH
(Connect to Queue and Download)
Readings
Events LP
Events HP
Load Profile
GatewaySMMCxWS
(WebService Solicitudes)
SQL Loader (Oracle)
COPY (PostgreSQL)
IntegradorReinyecta
OK
Yes
File
No
Meters Field
IntegradorCallServices
File
Some Event Response
Integration Request
First Response
Integration Request
First Response
SQL Loader (Oracle)
COPY (PostgreSQL)
File
I3
I4
I2
I1
Old Version
Notes: The I1 interface receives the messages from EventHub. Readings, load profile, events and alarms.
The I2 interface persists the messages in each local integration database of the distributors. Oracle or PostgreSQL.
The I3 interface sends the messages to the SOAP Websevices or API Rest owned by the distributors.
The I4 interface sends the requests from the distributors own systems to the ePlus system, through SOAP webservice.
The I6 interface allows communication between the Management and Operation System with other systems and applications of the Distribution Company, with read and write permission in both directions, as appropriate.

## Slide 6
I6
I6
Cloud Queue
Integration Services
Enel Distibutor Legacy Systems
Legacy Integration
Database
AMI
System
SMMePlus Integration Platform
IntegradorEH
(Connect to Queue and Download)
Readings
Events LP
Events HP
Load Profile
GatewaySMMCxWS
(WebService Solicitudes)
SQL Loader (Oracle)
COPY (PostgreSQL)
IntegradorReinyecta
OK
Yes
File
No
Meters Field
IntegradorCallServices
File
Some Event Response
Integration Request
First Response
Integration Request
First Response
SQL Loader (Oracle)
COPY (PostgreSQL)
File
I8
I8
Actualización PFC

## Slide 7
UM
CONCENTRADOR
Sistema de Gestion y Operación
(HES)
DMZ
Router Externo
Módulo RF
Módulo RF
MóduloDDLC
Módulo DLC
Red IP Local
Red Celular
Operador
Red interna Enel
Conexión Ethernet
Local
Comunicación RF
Comunicación DLC
Instalación Subestación MT/BT
Cliente
Acceso Local
Conexión Ethernet Local
Sonda Óptica
Sonda Óptica
Bluetooth
I3
I4
I0
Sistema de Comunicaciones Solución Medidor ENEL
Actualización PFC

## Slide 8
GEMIS
LVM
DMZ
Router Externo
Módulo RF
Módulo RF
Módulo PLC
Módulo PLC
Red IP Local
Red Celular
Operador
Sistemas de
Medidas (HES)
Conexión Ethernet
Local
Comunicación RF
Comunicación PLC
PACK MONITOREO
UM
Maqueta LVM - SmartMeter
SL7000
RS232
Conexión Serie
IP Router: 10.117.65.XX
Puerto Servicio SL7000: XX
Puerto servicio LVM: 50000
50001
50002
50003
21
22
Starbeat
SMMePLUS

## Slide 9
UM
Sistema de Gestion y Operación
(HES)
DMZ
Router Externo
Red IP Local
Red Celular
Operador
Red interna Enel
Conexión Serial RS232/RS485
Instalación Subestación MT/BT
Acceso Local
Sonda Óptica
I2
I0
Sistema de Comunicaciones Solución Medidor Punto a Punto
Actualización PFC
Conexión Ethernet

## Slide 10
Notes: The I0 interface allows local communication with the Measurement Unit and, if it exists, with the Concentrator Unit. The permissions may only be read, or read and write, depending on the authorization of the authorized personnel.
Permissions are not defined at interface level, but, for each kind of activity, it’s possible to give/remove permissions to users.
The mobile application of SMMePlus manages local activities with meters, but doesn't manage local activities on concentrators yet.
The I1 interface enables the display of data from the Unit of Measure to the Visualizer, when applicable, and with read-only permission.
It’s possible to see values from the display of the meter
Interfaces I2, I3 and I4 allow communication between the Measurement Unit and the Management and Operation System, between the Measurement Unit and the Concentrator Unit and between the Concentrator Unit and the Management and Operation System, respectively.
All of them with read and write permissions in both directions, as appropriate.
DLMS is not managed in SMMePlus yet. It will be available in 2021.
The I5 interface allows the Distribution Company to save the required information in the Central Database, and to access it in order to guarantee its integrity.
Not clear
The I6 interface allows communication between the Management and Operation System with other systems and applications of the Distribution Company, with read and write permission in both directions, as appropriate.
Data collected by SMMePlus are pushed on Event Hub queues (Microsoft Azure) that are shared with distribution company. The integration service of local country has the key for connecting with the Event Hub with read-only permissions.
The data collected by SMMePlus are also pushed on csv files, shared with local country using a cloud storage (Microsoft Storage Account) that, now, are accessed with a connection string that allows readn and write control.
In order to specify read or write permission the “Shared access signature” property of Azure Storage Account could be used.
In the other direction (from local systems to SMMePlus), SMMePlus exposes a service in the intranet that is used to provision information and request activities.
The I7 interface allows communication between the Central Database and the Data and Report Warehouse, and with read-only permission.
Reports of the website uses the read-only replica of database
The I8 interface allows authorized Stakeholders access to information from the Central Database. They will have read-only permissions, and the collection of information may be automatic, scheduled and periodic, or upon request, as defined.
A specific table of read-only replica database is accessible from Stakeholders
The I9 and I10 interfaces will act as I7 and I8 interfaces, respectively, in case the Data Operator is created.
Not clear
The I11 and I12 interfaces enable communication between the value added electrical services and the SMMC and the systems and applications of the Distribution Company, respectively. Permissions may be read only, or read and deed, as appropriate, and must be authorized by the Superintendency. In any case, the Client and / or User must authorize the use of their data as established in Chapter 8 of this Technical Annex.
Not clear